Inspect and document Domestic Cold Water Service Connections by the following checklist.

| General |
| --- |
| Project Name | Engineer of Record |
| Project Number | General Contractor |
| Project Manager | Mechanical Contractor |
| Lateral, Underground Piping, Tunnel Piping |
| Records Review Initial Date DCW flow modeled & reviewed _________ Plan views and profiles reviewed _________ Product submittals reviewed for compliance _________ Contractor Certifications reviewed & filed _________ Hydrostatic test (per AWWA) records complete/filed (6 hrs @ 200 psig) _________ A/E Review/Authorization to put in service received _________ DW Pipe flushing & cleaning procedures (per AWWA) submitted, approved, filed _________ Fire Protection piping flushed (per NFPA) & witnessed by State Fire Marshall _________ Chlorination (per AWWA) results submitted & on file _________ | Mechanical, Piping Field Inspection Confirm buried depth is 48” minimum from top of surface Confirm clear distances from other utilities Confirm pipe size matches installation drawings & flow model Confirm bedding material is sand (per AWWA) Confirm that all pipe supports and bolting are in place per plan & manufacturer’s recommendations (torque) Inspect & confirm Fire Hydrant(s) installation Confirm Fire Hydrant(s) meet CFD requirements Fire Hydrant(s) flushed to remove debris Inspect anchors, thrust blocks (concrete), supports, & bolting Inspect valves & gauges Inspect valve gear boxes for lubrication Inspect meter installation (ESS) Piping seals through structural penetrations not leaking Poly pipe wrap installed (per AWWA) Disinfection of piping complete (per AWWA) Chlorinated water disposed of per regulations |
| Comments |
| BDS Div Compliance. yes no, state reason: |
| Signatures |
| Inspected by Date | Reviewed and Approved (with conditions) by Date |
| Final inspection (if conditionally approved) by Date | Final Review and Approval by Date |
| Energized by Date | cc: Distribution Manager, Shop Supervisor, OSU Utilities Project Representative |